## Slide 1: HVSSD Facility Planning Discussion June 13, 2024

## Slide 2: Current Capacities
Facility/Process | Nominal Capacity (MGD)
Treatment Lagoons | 2.43 (1.43 Cell1, 1.0 Cell 1A)
Winter Storage Lagoons | 1.96
Land Application Site | 1.85
Mechanical Plant | 2.0 (design) /1.5 (estimated)
Rapid Infiltration Basins | 2.0
Plant Design Capacity | 4.43
Plant Firm Capacity 2024 | 3.35
Average Daily Flow 2024 | 2.18

## Slide 3: Flow Projections vs Capacity
Chart: HVSSD WRF Facility Capacity vs Flow
| 2020 | 2030 | 2040 | 2050
Max Month Flow | 2.88 | 3.89 | 4.81 | 5.5
Firm Capacity | 3.35 | 3.35 | 3.35 | 3.35
Design Capacity | 4.34 | 4.34 | 4.34 | 4.34
Average Flow | 2.49 | 3.37 | 4.17 | 4.77

## Slide 4: Address short-term capacity needs =CIB Project
Bridge the gap between firm and design capacity
Roughly a 10-year solution
Contemplated prior to major odor concerns/public complaints
Did not consider screens/headworks project
Assumed capacity of mechanical plant was 1 MGD (50% of design)
Does not appear to consider long-term planning- post 2040/2050

## Slide 5
Mechanical Aeration Upgrade 1.5 MGD
Primary Clarifier #2
Solids Dewatering and Loadout
Secondary Clarifier #3
Anaerobic Digesters and Support Building
Blowers/Pumps Building
Solids Holding/ Blending Tanks
~3.0 MGD Capacity (2 trains @ 1.5 MGD each)
4.85 MGD Combined Capacity w/ Lagoons
High odor potential
Growing nearer to neighbors
Requires RIBs expansion – add 1 MGD
Continue to operate and maintain lagoons
Cost estimated >$50M
Increased O&M
Original mechanical plant nearing 30 years old- exceeding service life
Meets needs to approx. 2040 (10-Year solution)
Site Constraints/Boxed In - Where do we go from here?
Property Line
HP&L
Island Ditch
CIB Mechanical Upgrade

## Slide 6: CIB Project Reconsideration
Reduce the scope of CIB project to necessary near-term projects next 5-10 yrs
Original |  | Proposed | 
Project | Cost Opinion | Project | Cost Opinion
Midway Lift Station | $639,000 | Midway Lift Station | $1,250,000
New Farm Shop | $699,000 | Generator | $160,000
Laboratory Building | $620,000 | Headworks Upgrade | $1,700,000
Generator | $160,000 | Aeration Upgrade (Lagoon) | $1,500,000
Mechanical Plant Aeration Upgrade | $12,470,000 | Lagoon Dredging? | $6,000,000
Blowers (Lagoon) | $600,000 |  | 
Aeration Piping (Lagoons) | $450,000 |  | 
Total Cost | $15,638,000 | Total Cost (w/ Dredging) | $9,260,000
 |  | Total Costs (w/out Dredging) | $3,260,000

## Slide 7: Addressing Long-Term Needs
What happens after the CIB project?
  Lagoon/Land Application System
    Significant Expansion is Unlikely
    Maintain current system/capacity
    Age -nearly 45 years of service
    What is the fate of the lagoons and land application?
  Increasing Capacity = Mechanical Plant Expansion
    Expand existing system?
    Build a new parallel system?
    Go all mechanical treatment?

## Slide 8: Addressing Long-Term Needs – Effluent Disposal
Land Application
  Current System at Capacity
  Limited opportunity for significant expansion
RIB’s
  Planned expansion to double capacity to 4 MGD
  District owns land
  Regulatory uncertainty with expansion
    Stricter limits/requirements, anti-degradation
Reuse – Type 1
  Water Rights Challenges
  Public Perception/Acceptance
  Advanced Treatment Requirements
    Filtration/Membranes
    High Level Disinfection
  Winter Storage Required
  Pumping /Distribution Infrastructure
Provo River
  Advanced treatment required- membranes likely
  Costly O&M – chemicals and sludge (phosphorus removal)
  Public and water user pushback
Other?
  Recharge Wells

## Slide 9: Addressing Long-Term Needs – Solids Management
District has benefited hugely over the last 40+ years by not having to manage or dispose of solids
Solids management typically accounts for 40-60% of capital and O&M costs at a WRF
It is believed that the practice of disposing sludge from the mechanical plant in Cell 1 has exacerbated odor generation
Conceptual Options
  Continue disposal in lagoon – THIS OPTION ASSUMES THE LAGOON IS DREDGED, AERATION IS REPAIRED/UPGRADED AND REGULAR DREDGING OCCURS TO MANAGE SOLIDS ACCUMULATION
  Management and Disposal
    Solids Stabilization
      Class A or Exceptional Quality
      Class B
      Unclassified
    Thickening/Dewatering
      Sidestream Management
    Disposal
      Landfill
      Land Apply

## Slide 10: Addressing Long-Term Needs – Emerging Contaminants
Pharmaceuticals, EDC’s
PFAS
Microplastics

## Slide 11: Path Forward….
Facility Plan- Comprehensive
  Alternatives and costs- liquid and solids treatment
  Engage with regulatory agencies
  Disposal options and strategy
  Board workshops
  Public engagement/involvement
  Rates and Impact Fees
  Funding/financial
  Plan costs: $150,000 -$250,000